## TD COMPLETO
Device under Test DUT
Type | GERADOR SINCRONO
Description
User
Manufacturer
Location
SerialNo
InventoryNo
AuxiliaryTitle
Operator
Supervisor
JobNo
Notes
InsulationDefinition | Generators & Motors : Stator Bar
InsulationTemperature | 31,0 °C
AmbientTemperature | 26,0 °C
RelativeHumidity | 67 % r.h.
TemperatureCorrection | 1
Sequence
SqNr | Descr. | Voltage[V] | Frequency[Hz] | UST A | UST B | UST A&B | GST A&B | GSTg A | GSTg B | GSTg A&B | Diagram | Instruction
1 | Side | 5000 | 50 | x | x
2 | Side | 10000 | 50 | x | x
Measurements
Start Time | Descr. | Conn. | Label | U rms[V] | Ix rms[A] | Cs (Zx=Cs+Rs)[F] | DF % (tan d)[%] | Frequency[Hz] | Comment
2022-10-04 08:57 | Manual | GSTg A&B |  | 1499 | 0.11094 | 1.9517e-07 | 0.908 | 60.36
2022-10-04 08:57 | Manual | GSTg A&B |  | 1998 | 0.14794 | 1.9522e-07 | 0.931 | 60.36
2022-10-04 08:58 | Manual | GSTg A&B |  | 2498 | 0.18501 | 1.9527e-07 | 0.956 | 60.36
2022-10-04 08:58 | Manual | GSTg A&B |  | 2997 | 0.22205 | 1.9533e-07 | 0.982 | 60.36
2022-10-04 08:59 | Manual | GSTg A&B |  | 3497 | 0.25915 | 1.9539e-07 | 1.009 | 60.36
2022-10-04 08:59 | Manual | GSTg A&B |  | 3997 | 0.29626 | 1.9546e-07 | 1.038 | 60.36
2022-10-04 09:00 | Manual | GSTg A&B |  | 4497 | 0.33341 | 1.9551e-07 | 1.063 | 60.36
2022-10-04 09:00 | Manual | GSTg A&B |  | 4996 | 0.37059 | 1.9559e-07 | 1.093 | 60.36
2022-10-04 09:00 | Manual | GSTg A&B |  | 5496 | 0.40782 | 1.9567e-07 | 1.126 | 60.36
2022-10-04 09:01 | Manual | GSTg A&B |  | 5996 | 0.44511 | 1.9576e-07 | 1.16 | 60.36
2022-10-04 09:01 | Manual | GSTg A&B |  | 6494 | 0.48231 | 1.9585e-07 | 1.195 | 60.36
2022-10-04 09:01 | Manual | GSTg A&B |  | 6995 | 0.5198 | 1.9595e-07 | 1.229 | 60.36
2022-10-04 09:02 | Manual | GSTg A&B |  | 7493 | 0.5571 | 1.9605e-07 | 1.267 | 60.36
2022-10-04 09:02 | Manual | GSTg A&B |  | 7993 | 0.59459 | 1.9615e-07 | 1.303 | 60.36
2022-10-04 09:07 | Manual | GSTg A&B |  | 7506 | 0.55811 | 1.9607e-07 | 1.28 | 60.36
2022-10-04 09:07 | Manual | GSTg A&B |  | 7006 | 0.52067 | 1.9598e-07 | 1.246 | 60.36
2022-10-04 09:08 | Manual | GSTg A&B |  | 6506 | 0.48329 | 1.9589e-07 | 1.212 | 60.36
2022-10-04 09:08 | Manual | GSTg A&B |  | 6006 | 0.44594 | 1.958e-07 | 1.175 | 60.36
2022-10-04 09:09 | Manual | GSTg A&B |  | 5505 | 0.40858 | 1.9571e-07 | 1.143 | 60.36
2022-10-04 09:09 | Manual | GSTg A&B |  | 5005 | 0.37132 | 1.9563e-07 | 1.11 | 60.36
2022-10-04 09:09 | Manual | GSTg A&B |  | 4503 | 0.33397 | 1.9555e-07 | 1.078 | 60.36
2022-10-04 09:10 | Manual | GSTg A&B |  | 4003 | 0.29681 | 1.955e-07 | 1.051 | 60.36
2022-10-04 09:10 | Manual | GSTg A&B |  | 3503 | 0.25964 | 1.9544e-07 | 1.021 | 60.36
2022-10-04 09:10 | Manual | GSTg A&B |  | 3003 | 0.22251 | 1.9538e-07 | 0.994 | 60.36
2022-10-04 09:11 | Manual | GSTg A&B |  | 2502 | 0.18533 | 1.9532e-07 | 0.966 | 60.36
2022-10-04 09:11 | Manual | GSTg A&B |  | 2002 | 0.14825 | 1.9526e-07 | 0.941 | 60.36
2022-10-04 09:12 | Manual | GSTg A&B |  | 1501 | 0.11114 | 1.9522e-07 | 0.916 | 60.36
2022-10-04 09:12 | Manual | GSTg A&B |  | 0 | 0 | 0 | 0 | 0
2022-10-04 09:27 | Manual | GSTg A&B |  | 1479 | 0.10934 | 1.9488e-07 | 0.874 | 60.36
2022-10-04 09:27 | Manual | GSTg A&B |  | 1998 | 0.1477 | 1.9492e-07 | 0.895 | 60.36
2022-10-04 09:28 | Manual | GSTg A&B |  | 2498 | 0.18471 | 1.9496e-07 | 0.916 | 60.36
2022-10-04 09:28 | Manual | GSTg A&B |  | 2997 | 0.22167 | 1.9501e-07 | 0.937 | 60.36
2022-10-04 09:29 | Manual | GSTg A&B |  | 3497 | 0.25869 | 1.9506e-07 | 0.961 | 60.36
2022-10-04 09:29 | Manual | GSTg A&B |  | 3997 | 0.29577 | 1.9512e-07 | 0.986 | 60.36
2022-10-04 09:30 | Manual | GSTg A&B |  | 4497 | 0.33282 | 1.9516e-07 | 1.011 | 60.36
2022-10-04 09:30 | Manual | GSTg A&B |  | 4996 | 0.36991 | 1.9524e-07 | 1.043 | 60.36
2022-10-04 09:31 | Manual | GSTg A&B |  | 5496 | 0.40711 | 1.9532e-07 | 1.078 | 60.36
2022-10-04 09:31 | Manual | GSTg A&B |  | 5996 | 0.44432 | 1.9541e-07 | 1.118 | 60.36
2022-10-04 09:31 | Manual | GSTg A&B |  | 6495 | 0.48159 | 1.9551e-07 | 1.153 | 60.36
2022-10-04 09:32 | Manual | GSTg A&B |  | 6993 | 0.51877 | 1.9561e-07 | 1.193 | 60.36
2022-10-04 09:32 | Manual | GSTg A&B |  | 7493 | 0.55615 | 1.9571e-07 | 1.232 | 60.36
2022-10-04 09:33 | Manual | GSTg A&B |  | 7993 | 0.59361 | 1.9583e-07 | 1.281 | 60.36
2022-10-04 09:49 | Manual | GSTg A&B |  | 7506 | 0.55721 | 1.9574e-07 | 1.223 | 60.37
2022-10-04 09:50 | Manual | GSTg A&B |  | 7006 | 0.51983 | 1.9564e-07 | 1.188 | 60.37
2022-10-04 09:50 | Manual | GSTg A&B |  | 6505 | 0.4825 | 1.9555e-07 | 1.153 | 60.37
2022-10-04 09:50 | Manual | GSTg A&B |  | 6006 | 0.44521 | 1.9546e-07 | 1.118 | 60.37
2022-10-04 09:51 | Manual | GSTg A&B |  | 5505 | 0.40792 | 1.9537e-07 | 1.081 | 60.37
2022-10-04 09:51 | Manual | GSTg A&B |  | 5005 | 0.37071 | 1.9529e-07 | 1.046 | 60.37
2022-10-04 09:51 | Manual | GSTg A&B |  | 4503 | 0.33344 | 1.9521e-07 | 1.014 | 60.37
2022-10-04 09:52 | Manual | GSTg A&B |  | 4003 | 0.29632 | 1.9516e-07 | 0.986 | 60.37
2022-10-04 09:52 | Manual | GSTg A&B |  | 3503 | 0.25923 | 1.951e-07 | 0.958 | 60.37
2022-10-04 09:52 | Manual | GSTg A&B |  | 3002 | 0.22209 | 1.9505e-07 | 0.933 | 60.37
2022-10-04 09:53 | Manual | GSTg A&B |  | 2502 | 0.18504 | 1.95e-07 | 0.909 | 60.37
2022-10-04 09:53 | Manual | GSTg A&B |  | 2002 | 0.14803 | 1.9496e-07 | 0.888 | 60.37
2022-10-04 09:54 | Manual | GSTg A&B |  | 1501 | 0.11099 | 1.9492e-07 | 0.866 | 60.37
2022-10-04 09:54 | Manual | GSTg A&B |  | 0 | 0 | 0 | 0 | 0
2022-10-04 10:02 | Manual | GSTg A&B |  | 1479 | 0.10929 | 1.9486e-07 | 0.844 | 60.37
2022-10-04 10:03 | Manual | GSTg A&B |  | 1998 | 0.1477 | 1.9489e-07 | 0.862 | 60.37
2022-10-04 10:03 | Manual | GSTg A&B |  | 2498 | 0.18469 | 1.9493e-07 | 0.881 | 60.37
2022-10-04 10:04 | Manual | GSTg A&B |  | 2984 | 0.22063 | 1.9497e-07 | 0.901 | 60.37
2022-10-04 10:04 | Manual | GSTg A&B |  | 3497 | 0.25865 | 1.9501e-07 | 0.922 | 60.37
2022-10-04 10:05 | Manual | GSTg A&B |  | 3997 | 0.2957 | 1.9507e-07 | 0.947 | 60.37
2022-10-04 10:05 | Manual | GSTg A&B |  | 4497 | 0.33279 | 1.9513e-07 | 0.975 | 60.37
2022-10-04 10:06 | Manual | GSTg A&B |  | 4995 | 0.36979 | 1.9518e-07 | 1.003 | 60.37
2022-10-04 10:06 | Manual | GSTg A&B |  | 5496 | 0.40702 | 1.9526e-07 | 1.037 | 60.37
2022-10-04 10:06 | Manual | GSTg A&B |  | 5996 | 0.44424 | 1.9535e-07 | 1.073 | 60.37
2022-10-04 10:07 | Manual | GSTg A&B |  | 6495 | 0.48146 | 1.9544e-07 | 1.105 | 60.37
2022-10-04 10:07 | Manual | GSTg A&B |  | 6993 | 0.5186 | 1.9553e-07 | 1.139 | 60.37
2022-10-04 10:08 | Manual | GSTg A&B |  | 7493 | 0.55598 | 1.9563e-07 | 1.177 | 60.37
2022-10-04 10:08 | Manual | GSTg A&B |  | 7993 | 0.5934 | 1.9574e-07 | 1.219 | 60.37
2022-10-04 10:11 | Manual | GSTg A&B |  | 7506 | 0.55702 | 1.9567e-07 | 1.202 | 60.37
2022-10-04 10:11 | Manual | GSTg A&B |  | 7006 | 0.51967 | 1.9558e-07 | 1.17 | 60.37
2022-10-04 10:12 | Manual | GSTg A&B |  | 6506 | 0.48237 | 1.9549e-07 | 1.137 | 60.37
2022-10-04 10:12 | Manual | GSTg A&B |  | 6005 | 0.44508 | 1.954e-07 | 1.104 | 60.37
2022-10-04 10:12 | Manual | GSTg A&B |  | 5505 | 0.40782 | 1.9532e-07 | 1.071 | 60.37
2022-10-04 10:13 | Manual | GSTg A&B |  | 5005 | 0.37062 | 1.9524e-07 | 1.038 | 60.37
2022-10-04 10:13 | Manual | GSTg A&B |  | 4503 | 0.33335 | 1.9517e-07 | 1.005 | 60.37
2022-10-04 10:13 | Manual | GSTg A&B |  | 4003 | 0.29625 | 1.9511e-07 | 0.977 | 60.37
2022-10-04 10:14 | Manual | GSTg A&B |  | 3503 | 0.25916 | 1.9506e-07 | 0.947 | 60.37
2022-10-04 10:14 | Manual | GSTg A&B |  | 3002 | 0.22205 | 1.9501e-07 | 0.921 | 60.37
2022-10-04 10:15 | Manual | GSTg A&B |  | 2502 | 0.18502 | 1.9496e-07 | 0.898 | 60.37
2022-10-04 10:15 | Manual | GSTg A&B |  | 2001 | 0.14796 | 1.9492e-07 | 0.878 | 60.37
2022-10-04 10:15 | Manual | GSTg A&B |  | 1501 | 0.11096 | 1.9489e-07 | 0.859 | 60.37
2022-10-04 10:16 | Manual | GSTg A&B |  | 0 | 0 | 0 | 0 | 0
2022-10-04 10:34 | Manual | GSTg A&B |  | 1499 | 0.32626 | 5.7383e-07 | 0.807 | 60.37
2022-10-04 10:34 | Manual | GSTg A&B |  | 1998 | 0.43498 | 5.7392e-07 | 0.826 | 60.37
2022-10-04 10:35 | Manual | GSTg A&B |  | 2498 | 0.54392 | 5.7406e-07 | 0.849 | 60.37
2022-10-04 10:35 | Manual | GSTg A&B |  | 2998 | 0.6529 | 5.7421e-07 | 0.873 | 60.37
2022-10-04 10:36 | Manual | GSTg A&B |  | 3497 | 0.7619 | 5.7437e-07 | 0.9 | 60.37
2022-10-04 10:36 | Manual | GSTg A&B |  | 3997 | 0.8711 | 5.7455e-07 | 0.929 | 60.37
2022-10-04 10:37 | Manual | GSTg A&B |  | 4496 | 0.9801 | 5.7475e-07 | 0.958 | 60.37
2022-10-04 10:37 | Manual | GSTg A&B |  | 4996 | 1.0896 | 5.7497e-07 | 0.991 | 60.37
2022-10-04 10:37 | Manual | GSTg A&B |  | 5495 | 1.1988 | 5.7522e-07 | 1.026 | 60.37
2022-10-04 10:38 | Manual | GSTg A&B |  | 5995 | 1.3085 | 5.7548e-07 | 1.062 | 60.37
2022-10-04 10:38 | Manual | GSTg A&B |  | 6495 | 1.4185 | 5.7577e-07 | 1.099 | 60.37
2022-10-04 10:38 | Manual | GSTg A&B |  | 6995 | 1.5283 | 5.7606e-07 | 1.135 | 60.37
2022-10-04 10:39 | Manual | GSTg A&B |  | 7495 | 1.6383 | 5.7635e-07 | 1.173 | 60.37
2022-10-04 10:39 | Manual | GSTg A&B |  | 7994 | 1.7485 | 5.7667e-07 | 1.211 | 60.37
2022-10-04 10:43 | Manual | GSTg A&B |  | 7506 | 1.641 | 5.764e-07 | 1.184 | 60.37
2022-10-04 10:43 | Manual | GSTg A&B |  | 7007 | 1.531 | 5.7611e-07 | 1.149 | 60.37
2022-10-04 10:43 | Manual | GSTg A&B |  | 6504 | 1.4206 | 5.7582e-07 | 1.114 | 60.37
2022-10-04 10:44 | Manual | GSTg A&B |  | 6005 | 1.3108 | 5.7554e-07 | 1.077 | 60.37
2022-10-04 10:44 | Manual | GSTg A&B |  | 5505 | 1.2011 | 5.7528e-07 | 1.04 | 60.37
2022-10-04 10:44 | Manual | GSTg A&B |  | 5004 | 1.0914 | 5.7502e-07 | 1.005 | 60.37
2022-10-04 10:45 | Manual | GSTg A&B |  | 4504 | 0.982 | 5.7479e-07 | 0.97 | 60.37
2022-10-04 10:45 | Manual | GSTg A&B |  | 4003 | 0.8724 | 5.7459e-07 | 0.938 | 60.37
2022-10-04 10:46 | Manual | GSTg A&B |  | 3503 | 0.7631 | 5.7441e-07 | 0.908 | 60.37
2022-10-04 10:46 | Manual | GSTg A&B |  | 3003 | 0.654 | 5.7424e-07 | 0.881 | 60.37
2022-10-04 10:46 | Manual | GSTg A&B |  | 2502 | 0.54473 | 5.7408e-07 | 0.855 | 60.37
2022-10-04 10:47 | Manual | GSTg A&B |  | 2002 | 0.43579 | 5.7395e-07 | 0.832 | 60.37
2022-10-04 10:47 | Manual | GSTg A&B |  | 1501 | 0.32672 | 5.7382e-07 | 0.809 | 60.37
2022-10-04 10:47 | Manual | GSTg A&B |  | 0 | 0 | 0 | 0 | 0